## Sheet1
Community | Total Number of generators | Total Capacity (in kW) | Largest generator (in kW) | Sizing | Number to replace ("Poor") | Switchgear Suitable | Waste Heat Recovery Opperational | Add waste heat Avail | Est. current annual heating fuel gallons displaced | Est. potential annual heating fuel gallons displaced | Distance of Piping Needed (ft) | Number of Buildings to connect | Waste Heat Available (in gallons of heating oil equivalent) | Capital Costs (if known) | Operational Costs (if known)
Adak | 5 | 4035 | 1135 | undersized & oversized | 4 | No | No | No | N/A | N/A
Akhiok | 3 | 267 | 117 | properly sized | 0 | No | No | No | unknown | unknown
Akiachak | 4 | 1450 | 475 | properly sized | 0 | Yes | Yes | Yes | N/A | N/A
Akiak | 4 | 920 | 230 | properly sized | 0 | Yes | Yes | Yes | N/A | N/A
Akutan | 3 | 417 | 150 | properly sized | 1 | No | No | No | N/A | N/A
Alakanuk | 3 | 1150 | 500 | properly sized | 0 | No | Yes | No | unknown | unknown
Allakaket | 3 | 525 | 175 | oversized | 0 | No | Yes | Yes | unknown | unknown
Ambler | 3 | 1040 | 400 | properly sized | 0 | No | No | No | unknown | unknown
Anaktuvuk Pass | 5 | 2810 | 910 | undersized | 0 | Yes | Yes | Yes | unknown | unknown
Angoon | 3 | 1525 | 550 | oversized | 0 | Yes | Yes | Yes | 0 | 0
Aniak | 2 | 1100
Anvik | 3 | 375 | 160 | properly sized | 0 | No | Yes | No | unknown | unknown
Arctic Village | 4 | 395 | 130 | properly sized | 1 | Yes | Yes | Yes | unknown | unknown
Atka | 3 | 257 | 110 | properly sized | 1 | No | No | No | N/A | N/A
Atmautluak | 3 | 547 | 250 | properly sized | 0 | Yes | No | No | N/A | N/A
Atqasuk | 6 | 4100
Barrow
Beaver | 3 | 244 | 110 | properly sized | 2 | Yes | Yes | Yes | 18250 | none
Bethel | 6 | 13500 | 2250 | properly sized | 0 | No | Yes | Yes | unknown | unknown
Bettles | 3 | 600 | 300 | properly sized | 0 | No | No | No | N/A | N/A
Birch Creek | 1 | 28 | 28 | properly sized | 0 | No | No | No | N/A | N/A
Brevig Mission | 3 | 1025 | 500 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Buckland | 3 | 1132 | 476 | properly sized | 0 | Yes | Yes | Yes | see notes | nee notes
Central | 3 | 575 | 200 | properly sized | 0 | No | Yes | No | unknown | unknown
Chalkyitsik | 3 | 307 | 125 | properly sized | 1 | No | Yes | No | unknown | unknown
Chefornak | 3 | 921 | 371 | properly sized | 0 | Yes | Yes | No | N/A | N/A
Chenega Bay | 3 | 175 | 65 | undersized | 0 | Yes | Yes | No | unknown | unknown
Chevak | 3 | 1615 | 660 | properly sized | 0 | Yes | Yes | Yes | N/A | N/A
Chignik | 3 | 577 | 230 | undersized | 0 | Yes | Yes | No | N/A | N/A
Chignik Lagoon | 3 | 453 | 160 | oversized | 0 | Yes | Yes | No | unknown | unknown
Chignik Lake | 4 | 442 | 147 | properly sized | 3 | Yes | Yes | No | unknown | unknown
Chilkat Valley | 1 | 600 | 600 | oversized | 1 | No | No | No | unknown | unknown
Chistochina | 2 | 200 | 100 | properly sized | 0 | No | No | No | N/A | N/A
Chitina | 3 | 301 | 117 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Chuathbaluk | 3 | 179 | 78 | undersized | 0 | Yes | No | No | 0 | 0
Circle | 2 | 188 | 98 | properly sized | 1 | No | No | No | N/A | N/A
Clarks Point | 3 | 476 | 250 | properly sized | 0 | No | Yes | No | unknown | unknown
Coffman Cove | 2 | 660 | 330 | properly sized | 0 | Yes | No | No | unknown | unknown
Cold Bay | 3 | 2600 | 875 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Cordova | 5 | 10853 | 3700 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Craig | 4 | 4545 | 1630 | oversized | 0 | Yes | No | No | unknown | unknown
Crooked Creek | 3 | 223 | 95 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Deering | 4 | 577 | 170 | oversized | 0 | Yes | Yes | No | unknown | unknown
Dillingham | 7 | 6600 |  |  |  | Yes | Yes | nO
Diomede
Eagle | 3 | 450 | 175 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Eek | 3 | 541 | 206 | properly sized | 0 | No | Yes | No | N/A | N/A
Egegik | 2 | 380 | 200 | properly sized | 0 | No | No | No | N/A | N/A
Ekwok | 3 | 370 | 220 | properly sized | 0 | No | No | No | N/A | N/A
Elfin Cove | 3 | 347 | 179 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Elim | 3 | 1050 | 500 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Emmonak | 4 | 1920 | 915 | properly sized | 0 | Yes | Yes | No | unknown | unknown
False Pass | 3 | 375 | 175 | properly sized | 0 | No | Yes | No | 12775 | unknown
Fasle Island | 1 | 1200 | 1200 | undersized | 0 | Yes | No | No | unknown | unknown
Fort Yukon | 4 | 2070 | 600 | properly sized | 0 | No | No | No | N/A | N/A
Galena | 6 | 4600 | 1050 | properly sized | 2 | No | Yes | No | 36500 | unknown
Gambell | 3 | 1600
Glennallen | 7 | 10700
Golovin | 4 | 580 | 200 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Goodnews Bay | 3 | 643 | 268 | properly sized | 0 | No | Yes | Yes | N/A | N/A
Grayling | 3 | 260 | 155 | properly sized | 0 | No | No | No | N/A | N/A
Gustavus | 3 | 842 | 371 | properly sized | 0 | Yes | No | No | unknown | unknown
Haines | 4 | 6200
Healy Lake | 2 | 83 | 50 | oversized | 0 | Yes | No | No | N/A | N/A
Hollis | 1 | 450 | 450 | undersized | 0 | No | No | No | unknown | unknown
Holy Cross | 3 | 455 | 155 | properly sized | 0 | No | No | No | 0 | 0
Hoonah | 3 | 2000
Hooper Bay | 4 | 2178 | 828 | properly sized | 0 | Yes | Yes | No | N/A | N/A
Hughes | 4 | 230 | 78 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Huslia | 3 | 728 | 268 | properly sized | 0 | No | Yes | No | unknown | unknown
Hydaburg | 3 | 1205 | 560 | properly sized | 0 | Yes | No | Yes | unknown | unknown
Igiugig | 3 | 201 | 67 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Ivanof Bay | 3 | 224 | 92 |  | 3 | No | No | No | N/A | N/A
Juneau | 19 | 106000
Kake | 3 | 2431 | 1016 | oversized | 0 | No | No | No | unknown | unknown
Kaktovik | 4 | 3090 | 910 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Kaltag | 3 | 549 | 325 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Karluk | 2 | 100 | 50 | properly sized | 0 | No | No | No | unknown | unknown
Kasaan | 2 | 345 | 250 | properly sized | 0 | No | No | No | unknown | unknown
Kasigluk | 3 | 1575 | 750 | properly sized | 0 | Yes | Yes | Yes | N/A | N/A
Ketchikan | 4 | 25900
Kiana | 3 | 1195 | 500 | oversized | 0 | No | Yes | No | unknown | unknown
King Cove | 4 | 2700 | 1050 | properly sized | 0 | Yes | Yes | Yes | work being completed | none
Kipnuk | [5 empty] | Yes | Yes | No
Kivalina | 4 | 1160 | 350 | properly sized | 2 | No | Yes | No | operator new, not aware AVEC has records | operator new, not aware AVEC has records
Klawock | 1 | 1000
Kobuk | 1 | 215 | 215 | properly sized | 0 | No | No | No | N/A | N/A
Kodiak | 12 | 33300
Kokhanok | 4 | 452 | 160 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Koliganek | 2 | 420 | 220 | properly sized | 1 | No | Yes | No | unknown | unknown
Kongiganak | 4 | 985 | 250 | properly sized | 0 | No | Yes | Yes | unknown | unknown
Kotlik | 4 | 1700 | 500 | properly sized | 1 | Yes | Yes | No | unknown | unknown
Kotzebue | 5 | 11100
Koyuk | 3 | 1150 | 500 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Koyukuk | 4 | 202 | 64 | properly sized | 1 | Yes | Yes | Yes | 18250 | none
Kwethluk | 3 | 1100 | 410 | properly sized | 0 | Yes | Yes | Yes | N/A | N/A
Kwigillingok | 4 | 723 | 275 | properly sized | 0 | No | Yes | Yes | 0 | 0
Larsen Bay | 2 | 360 | 180 | oversized | 1 | No | No | No | 0 | 0
Levelock | 3 | 234 | 100 | properly sized | 0 | Yes | Yes | Yes | 9300 | 900
Lime Village
Manley Hot Springs | 3 | 480 | 250 | oversized | 0 | No | Yes | No | unknown | unknown
Manokotak | 4 | 830 | 260 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Marshall | 3 | 1085 | 500 | properly sized | 0 | No | Yes | No | unknown | unknown
McGrath | 4 | 2140 | 670 | properly sized | 1 | No | Yes | No | 60000 | unknown
Mekoryuk | 3 | 704 | 268 | properly sized | 0 | Yes | Yes | No | N/A | N/A
Metlakatla | 1 | 3300
Minto | 3 | 708 | 268 | oversized | 0 | No | Yes | Yes | unknown | unknown
Mountain Village | 4 | 1990 | 750 | undersized | 0 | No | Yes | No | unknown | unknown
Naknek | 10 | 9900 |  |  |  | Yes | Yes | No
Napakiak | 1 | 250 | 250 | properly sized | 0 | No | No | No | N/A | N/A
Napaskiak | 3 | 577 | 230 | properly sized | 0 | Yes | No | No | N/A | N/A
Naukati Bay | 3 | 488 | 175 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Nelson Lagoon | 3 | 295 | 110 | properly sized | 1 | Yes | No | No | N/A | N/A
New Stuyahok | 3 | 1331 | 500 | properly sized | 0 | No | Yes | No | unknown | unknown
Newhalen | 4 | 1560 | 600 | properly sized | 0 | No | Yes | Yes | 5000 | 16000
Newtok | [5 empty] | No
Nightmute | 1 | 325 | 325 | properly sized | 0 | No | No | No | N/A | N/A
Nikolai | 3 | 300 | 100 | properly sized | 0 | No | No | No | N/A | N/A
Nikolski | 3 | 196 | 71 | properly sized | 0 | Yes | Yes | No | 660 | none
Noatak | 3 | 1184 | 500 | oversized | 1 | No | No | No | unknown | unknown
Nome | 5 | 16357 | 5211 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Noorvik | 3 | 1614 | 750 | properly sized | 2 | No | No | No | N/A | N/A
Northway | 3 | 1030 | 400 | oversized | 0 | Yes | No | No | N/A | N/A
Nuiqsut | 5 | 3910 | 910 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Nulato | 3 | 1002 | 376 | properly sized | 0 | No | Yes | No | 7300 | none
Nunam Iqua | 3 | 708 | 250 | undersized & oversized | 0 | No | Yes | No | 9000 | unknown
Nunapitchuk | 1 | 500 | 500 | properly sized | 0 | No | Yes | No | N/A | N/A
Old Harbor | 3 | 530 | 200 | properly sized | 0 | No | No | No | N/A | N/A
Ouzinkie | 3 | 335 | 190 | properly sized | 0 | Yes | No | No | 0 | 0
Pedro Bay | 3 | 211 | 95 | properly sized | 0 | Yes | No | No | N/A | N/A
Pelican | 3 | 921 | 371 | properly sized | 0 | Yes | No | No | unknown | unknown
Perryville | 3 | 473 | 175 | properly sized | 0 | No | Yes | Yes | 10950 | unknown
Petersburg | 8 | 32000
Pilot Point | 3 | 246 | 101 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Pilot Station | 3 | 1200
Pilot Station | 3 | 1202 | 450 | properly sized | 0 | No | No | No | 0 | 0
Platinum | 2 | 129 | 75 | properly sized | 0 | No | Yes | No | N/A | 0
Point Hope | 4 | 3100
Point Lay | 4 | 2400
Port Alsworth | 3 | 466 | 187 | properly sized | 0 | No | Yes | No | 14600 | 2500
Port Heiden | 2 | 369 | 190 | properly sized | 1 | No | Yes | No | unknown | unknown
Quinhagak | 3 | 1212 | 499 | oversized |  | Yes | No | Yes | unknown | unknown
Rampart | 3 | 367 | 187 | properly sized | 1 | No | No | No | unknown | unknown
Red Devil | 3 | 130 | 50 | properly sized | 3 | No | No | No | 0 | 0
Ruby | 3 | 470 | 230 | properly sized | 0 | Yes | Yes | Yes | 14600 | 3650
Russian Mission | 3 | 904 | 376 | properly sized | 0 | No | Yes | No | unknown | unknown
Saint George | 4 | 890 | 330 | properly sized | 2 | No | No | No | N/A | N/A
Saint Mary's | 3 | 2175 | 915 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Saint Michael | 3 | 1060 | 500 | properly sized | 1 | No | No | No | N/A | N/A
Saint Paul | 5 | 2920 | 855 | oversized | 0 | No | Yes | No | unknown | unknown
Sand Point | 4 | 2880 | 900 | properly sized | 0 | Yes | Yes | No | 3650 | 18250
Savoonga | 3 | 1523 | 660 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Scammon Bay | 3 | 1285 | 660 | properly sized | 0 | No | Yes | No | N/A | N/A
Selawik | 3 | 1625 | 800 | properly sized | 1 | Yes | Yes | Yes | unknown | unknown
Shageluk | 3 | 407.5 | 190 | properly sized | 0 | No | Yes | No | unknown | unknown
Shaktoolik | 3 | 998 | 470 | oversized | 0 | Yes | Yes | No | unknown | unknown
Shishmaref | 4 | 1576 | 500 | properly sized | 2 | No | Yes | No | unknown | unknown
Shungnak | 4 | 1317 | 400 | properly sized | 0 | No | Yes | No | unknown | unknown
Sitka | 5 | 25600
Skagway | 4 | 3400
Slana | 3 | 730 | 275 | properly sized | 0 | Yes | Yes | No | unknown | unknown
Sleetmute | 4 | 323 | 110 | properly sized | 0 | Yes | No | No | 0 | 0
Stebbins | 3 | 1100 | 500 | properly sized | 1 | No | No | No | N/A | N/A
Stevens Village | 4 | 258 | 95 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Stony River | 3 | 138 | 64 | properly sized | 0 | Yes | No | No | 0 | 0
Takotna | 4 | 216 | 78 | properly sized | 3 | No | No | No | N/A | N/A
Tanana | 4 | 1605 | 680 | properly sized | 0 | No | Yes | Yes | unknown | unknown
Tatitlek | 3 | 315 | 125 | properly sized | 2 | No | No | No | unknown | unknown
Telida | 3 | 28 | 28 |  | 3 | No | No | No | N/A | N/A
Teller | 6 | 1050 | 297 | properly sized | 3 | No | No | No | N/A | N/A
Tenakee Springs | 3 | 240 | 88 | properly sized | 0 | Yes | No | No | unknown | unknown
Thorne Bay | 2 | 1075 | 650 | properly sized | 0 | Yes | No | No | unknown | unknown
Togiak | 3 | 1628 | 828 | properly sized | 0 | No | Yes | No | unknown | unknown
Tok | 6 | 7010 | 1930 | oversized | 0 | No | Yes | No | unknown | unknown
Toksook Bay | 3 | 1531 | 756 | properly sized | 0 | Yes | Yes | Yes | N/A | N/A
Tuluksak | 4 | 795 | 290 | properly sized | 4 | No | No | No | N/A | N/A
Tuntutuliak | 4 | 802 | 250 | properly sized | 0 | No | No | No | 0 | 0
Tununak | 1 | 325 | 325 | properly sized | 0 | No | No | No | N/A | N/A
Twin Hills | 2 | 220 | 128 | properly sized | 0 | No | No | No | N/A | N/A
Unalakleet | 4 | 1820 | 455 | properly sized | 0 | Yes | Yes | Yes | unknown | unknown
Unalaska | 7 | 19060 | 5400 | properly sized | 0 | No | Yes | No | unknown | unknown
Upper Kalskag | 3 | 1100 | 325 | properly sized | 0 | Yes | No | No | unknown | unknown
Valdez | 8 | 15000 |  |  |  | Yes | Yes
Venetie | 3 | 495 | 190 | properly sized | 0 | No | Yes | No | 2000 | unknown
Wainwright | 5 | 3110 | 910 | undersized | 0 | Yes | Yes | Yes | unknown | unknown
Wales | 3 | 495 | 200 | properly sized | 0 | No | No | No | unknown | unknown
Whale Pass | 3 | 250 | 110 | properly sized | 0 | Yes | Yes | No | unknown | unknown
White Mountain | 3 | 585 | 275 | properly sized | 1 | Yes | Yes | No | unknown | unknown
Wrangell | 4 | 8500
Yakutat | 5 | 6715 | 1855 | oversized | 1 | Yes | Yes | Yes | unknown | unknown